## 160 Spear
Building Level Interventions
Instructions: Enter any identified building-level interventions that impact energy usage and emissions. Interventions may include operational changes, retrofits, enhancements to existing capital plans, electrification, and on-site renewables. All boxes for a given intervention should be populated. To optimize for user friendliness, order the interventions based on the earliest possible year of intervention, moving from earliest to latest. Interventions should be identified by the building's engineering team in coordination with Paul Rode and the TS sustainability team. Formatting: Additional Up-Front Costs and Additional Opex should be stated in negative terms and should be priced on a "relative to business as usual" basis (i.e. only state the price in excess of a business as usual scenario). If there is no lifespan, enter "No Lifespan" to indicate this. If the building does not use a certain energy type, enter "0" for the expected reduction. Change in energy consumption should be entered as a negative value if there is a reduction in consumption associated with the intervention and as a positive value if there will be an increase in consumption. If there is an earliest possible date when an intervention can be launched, enter this year in the "Earliest Possible Date" column. If not, enter the current year in this field.
Order | Intervention Name | Description of Measure | Intervention Type | Additional Up-Front Cost (Net rebates from utilities or state energy offices, or federal programs) | Up Front Cost: Capex or R&M | Change in Electricity Consumption Reduction (kWh) | Change in Natural Gas Use(MMBtu) | Change in Steam Consumption, kLbs | Useful Life/Lifespan | Earliest Possible Year | Change in Opex (O&M) | Energy Savings Passthrough? | Sources (Citations, Links, Consulting Reports, etc.)
1 | Retrocommissioning (RCx) | Complete BMS commissioning | Retrofit | 35000 | R&M | 61280.2931 | 61943.6292 | - | 10 | 2025 | $- | No | RCx proposals
7 | Elevator energy revovery | Optional add to elevator package | Capital Project Enhancement | 120000 | Capex | 13590.8596 | 26675.1433 | - | 25 | 2035 | $- | No | Schindler
5 | New Electric Chillers | Chiller Plant | Capital Project Enhancement | 650000 | Capex | 84122.9745 | 0 | - | 25 | 2028 | -25000 | No | Train
2 | DHW to Point of Use | Electrificaiton | Electrification | 85000 | Capex | -39088.4213 | 133.3757 | - | 10 | 2024 | $- | No | Eng
3 | Façade air stopping | caulking and general air stopping | Retrofit | 1000000 | R&M | 14228.1218 | 18386.175 | - | 20 | 2023 | $- | No | Eng
4 | New High Efficiency Windows | New Windows tripple pane R6@30SHG | Capital Project Enhancement | 10000000 | Capex | 8110.0294 | 10480.1198 | - | 40 | 2028 | $- | No | Eng
8 | Central ASHP to Hot Water | Electrificaiton | Electrification | 2750000 | Capex | -238865.815 | 2852.6644 | - | 20 | 2030 | -35000 | No | Eng
8 | Electric Boiler | Electrificaiton | Electrification | 1500000 | Capex | -836030.3524 | 2852.6644 | - | 20 | 2026 | -5000 | No | Eng
6 | Pneumatic Converstion | BMS Expansion | Capital Project Enhancement | 230000 | Capex | 1781.0131 | 20331.4323 | - | 15 | 2030 | $- | No | Delta Controls

## 333 Bush
Building Level Interventions
Instructions: Enter any identified building-level interventions that impact energy usage and emissions. Interventions may include operational changes, retrofits, enhancements to existing capital plans, electrification, and on-site renewables. All boxes for a given intervention should be populated. To optimize for user friendliness, order the interventions based on the earliest possible year of intervention, moving from earliest to latest. Interventions should be identified by the building's engineering team in coordination with Paul Rode and the TS sustainability team. Formatting: Additional Up-Front Costs and Additional Opex should be stated in negative terms and should be priced on a "relative to business as usual" basis (i.e. only state the price in excess of a business as usual scenario). If there is no lifespan, enter "No Lifespan" to indicate this. If the building does not use a certain energy type, enter "0" for the expected reduction. Change in energy consumption should be entered as a negative value if there is a reduction in consumption associated with the intervention and as a positive value if there will be an increase in consumption. If there is an earliest possible date when an intervention can be launched, enter this year in the "Earliest Possible Date" column. If not, enter the current year in this field.
Order | Intervention Name | Description of Measure | Intervention Type | Additional Up-Front Cost (Net rebates from utilities or state energy offices, or federal programs) | Up Front Cost: Capex or R&M | Change in Electricity Consumption Reduction (kWh) | Change in Natural Gas Use(MMBtu) | Change in Steam Consumption, kLbs | Useful Life/Lifespan | Earliest Possible Year | Change in Opex (O&M) | Energy Savings Passthrough? | Sources (Citations, Links, Consulting Reports, etc.)
1 | Optimun Start / Stop | Controls with ML program | Retrofit | 118000 | R&M | 25570.275 | 56093.5372 | 0 | 12 | 2024 | 0 | No | Eng
2 | Pumping Optizamation | VFD's Controls with ML program | Retrofit | 225000 | Capex | 24291.761 | 53288.8603 | 0 | 12 | 2024 | 0 | No | Eng
3 | Back of house lighting | Optional add to elevator package | Retrofit | 80000 | Capex | 23284.963 | 0 | 0 | 12 | 2024 | 0 | No | PR
4 | Limited Façade Air Stopping | Insulation and wet sealing | Retrofit | 2250000 | Capex | 9230.869 | 20249.7669 | 0 | 40 | 2030 | -10000 | No | Eng
5 | Airside energy recovery | Run Arouind Coils | Capital Project Enhancement | 850000 | Capex | 45231.26 | 99223.8579 | 0 | 30 | 2024 | 0 | No | Eng
6 | Chiller plant optimization | Controls with ML program | Retrofit | 60000 | R&M | 15409.472 | 0 | 0 | 12 | 2024 | 0 | No | Eng
7 | Water soruced heat recovery | Electrificaiton | Electrificaiton | 300000 | Capex | -10123.34 | 120.8984 | 0 | 25 | 2027 | 6000 | No | York
8 | Window Retrofit | New window film | Retrofit | 750000 | R&M | 7833.437 | 0 | 0 | 35 | 2030 | 0 | No | 3M
9 | Chiller end of life replacement | Chiller plan replacement | Capital Project Enhancement | 2500000 | Capex | 27182.309 | 0 | 0 | 25 | 2030 | 0 | No | York
10 | Elevator energy revovery | Elevator Mod with energy recovery | Capital Project Enhancement | 240000 | R&M | 46337.077 | 0 | 0 | 25 | 2035 | 0 | No | Schindler
11 | Heating Electrification via ASHP's | Electrificaiton | Electrificaiton | 8000000 | R&M | -24296.017 | 290.1561 | 0 | 20 | 2035 | 24000 | No | TS