## One Fed
Building Level Interventions
Instructions: Enter any identified building-level interventions that impact energy usage and emissions. Interventions may include operational changes, retrofits, enhancements to existing capital plans, electrification, and on-site renewables. All boxes for a given intervention should be populated. To optimize for user friendliness, order the interventions based on the earliest possible year of intervention, moving from earliest to latest. Interventions should be identified by the building's engineering team in coordination with Paul Rode and the TS sustainability team. Formatting: Additional Up-Front Costs and Additional Opex should be stated in negative terms and should be priced on a "relative to business as usual" basis (i.e. only state the price in excess of a business as usual scenario). If there is no lifespan, enter "No Lifespan" to indicate this. If the building does not use a certain energy type, enter "0" for the expected reduction. Change in energy consumption should be entered as a negative value if there is a reduction in consumption associated with the intervention and as a positive value if there will be an increase in consumption. If there is an earliest possible date when an intervention can be launched, enter this year in the "Earliest Possible Date" column. If not, enter the current year in this field.
Building | Savings | Order | Intervention Name | Description of Measure | Intervention Type | Additional Up-Front Cost (Net rebates from utilities or state energy offices, or federal programs) | Up Front Cost: Capex or R&M | Change in Electricity Consumption Reduction (kWh) | Change in Natural Gas Use(MMBtu) | Change in Steam Consumption, kLbs | Useful Life/Lifespan | Earliest Possible Year | Change in Opex (O&M) | Energy Savings Passthrough? | Sources (Citations, Links, Consulting Reports, etc.)
222 Second Street | Heating & Cooling | 1 | Retrocommissioning (RCx) | Implement ECMs from ComEd report | Retrofit + Training |  |  | 0.04
222 Second Street | Heating & Cooling & Base | 2 | Technology enablement - Access control Converge Network People counters |  | Capital Project |  |  | 0
222 Second Street | Heating & Cooling | 3 | BMS Expansion and optimizations | Chiller plant instrumentation | Capex |  |  | 0.03
222 Second Street | Cooling | 4 | CHW Pumping VFD Retrofit | Add FVD's to CHW and CW pumps | Capex |  |  | 0.02
222 Second Street | Heating & Cooling | 5 | Fan powered box retrofit | Add DDC, ECM Motors and sensors | Capital Project Enhancement |  |  | 0.004
222 Second Street | Heating & Cooling | 6 | Façade / Window air stopping | caulking and general air stopping | Retrofit |  |  | 0.02
222 Second Street | Base | 7 | Elevator energy revovery | Optional add to elevator package | Capital Project Enhancement |  |  | 0.001
222 Second Street | Heating & Cooling | 8 | Roof replacment | EOL replacement adding insulation | Capital Project |  |  | 0.0001
222 Second Street | Base | 9 | Solar | Rooftop solar | Capital Project |  |  | 0.01
222 Second Street | Base | 9.1 | POU hot water heaters | Restroom DHW POU with planed refresh | Capital Project Enhancement |  |  | 0.3
222 Second Street | Heating | 9.2 | Heat recovery for winter operation | AHU Recovery coils for OA | Capital Project |  |  | 0.1
222 Second Street | Heating & Cooling | 9.3 | New High Efficiency Windows | High Eff Windows | Capital Project |  |  | 0.02
222 Second Street | Cooling | 9.4 | New High Efficiency Electric 1300ton Chiller | Chiller EOL Replacement | Capital Project Enhancement |  |  | 0.15

## Sheet1
Heating
Cooling
Base
Heating & Cooling
Heating & Cooling & Base

## 222 Second
Savings | Order | Intervention Name | Description of Measure | Intervention Type | Additional Up-Front Cost (Net rebates from utilities or state energy offices, or federal programs) | Up Front Cost: Capex or R&M | Change in Electricity Consumption Reduction (kWh)
Heating & Cooling | 1 | Retrocommissioning (RCx) | Implement ECMs from ComEd report | Retrofit + Training | 48000 | R&M | 138708
Heating & Cooling & Base | 2 | Technology enablement - Access control Converge Network People counters |  | Capital Project | 2083660 | Capex | 0
Heating & Cooling | 3 | BMS Expansion and optimizations | Chiller plant instrumentation | Capex | 500000 | Capex | 2059819
Cooling | 4 | CHW Pumping VFD Retrofit | Add FVD's to CHW and CW pumps | Capex | 275000 | Capex | 230692
Heating & Cooling | 5 | Fan powered box retrofit | Add DDC, ECM Motors and sensors | Capital Project Enhancement | 2880000 | Capex | 572081
Heating & Cooling | 6 | Façade / Window air stopping | caulking and general air stopping | Retrofit | 1300000 | R&M | 108695
Base | 7 | Elevator energy revovery | Optional add to elevator package | Capital Project Enhancement | 120000 | Capex | 19881
Heating & Cooling | 8 | Roof replacment | EOL replacement adding insulation | Capital Project | 7958000 | Capex | 215217
Base | 9 | Solar | Rooftop solar | Capital Project | 400000 | Capex | 169502
Base | 9.1 | POU hot water heaters | Restroom DHW POU with planed refresh | Capital Project Enhancement | 196000 | Capex | 16093
Heating | 9.2 | Heat recovery for winter operation | AHU Recovery coils for OA | Capital Project | 2100000 | Capex | 32529
Heating & Cooling | 9.3 | New High Efficiency Windows | High Eff Windows | Capex | 54100000 | Capex | 525655
Cooling | 9.4 | New High Efficiency Electric 1300ton Chiller | Chiller EOL Replacement | Capital Project Enhancement | 1950000 | Capex | 383791

## 160 Spear
Building | Savings | Order | Intervention Name | Description of Measure | Intervention Type | Additional Up-Front Cost (Net rebates from utilities or state energy offices, or federal programs) | Up Front Cost: Capex or R&M | Change in Electricity Consumption Reduction (kWh) | Change in Natural Gas Use(MMBtu) | Change in Steam Consumption, kLbs | Useful Life/Lifespan
160 Spear | Heating & Cooling & Base | 1 | Retrocommissioning (RCx) | Complete BMS commissioning | Retrofit | 35000 | R&M | 0.04 | 0.04 | -
160 Spear | Base | 7 | Elevator energy revovery | Optional add to elevator package | Capital Project Enhancement | 120000 | Capex | 0.01 | 0 | -
160 Spear | Cooling | 5 | New Electric Chillers | Chiller Plant | Capital Project Enhancement | 650000 | Capex | 0.1 | 0 | -
160 Spear | Base | 2 | DHW to Point of Use | Electrificaiton | Electrification | 85000 | Capex | 0.5 | 0.5 | -
160 Spear | Heating & Cooling | 3 | Façade air stopping | caulking and general air stopping | Retrofit | 1000000 | R&M | 0.02 | 0.02 | -
160 Spear | Heating & Cooling | 4 | New High Efficiency Windows | New Windows tripple pane R6@30SHG | Capital Project Enhancement | 10000000 | Capex | 0.05 | 0.05 | -
160 Spear | Heating & Cooling & Base | 8 | Central ASHP to Hot Water | Electrificaiton | Electrification | 2750000 | Capex | 3 | 1 | -
160 Spear | Heating & Cooling & Base | 8 | Electric Boiler | Electrificaiton | Electrification | 1500000 | Capex | 1 | 1 | -
160 Spear | Heating & Cooling | 6 | Pneumatic Converstion | BMS Expansion | Capital Project Enhancement | 230000 | Capex | 0.02 | 0.02 | -
160 Spear | Heating & Cooling & Base | 8 | Test Name | Electrificaiton | Capital Project Enhancement | 1000000 | Capex | 1 | 1 | -