## Sheet2
| Building | SQFT | Code | Load | Base Loads | Cooling Loads |  | Heating Loads | CheckSum |  | Fm Savings | Intervention Name | Savings | Order | Description of Measure | Change in Electricity Consumption Reduction (kWh) | Change in Natural Gas Use(MMBtu) | Change in Steam Consumption, kLbs | Saved_Base | Saved_Cooling | Ck Cooling | Saved_Heating | Ck Heating
1 | 222 N LaSalle | 1018838 | EEEO | Elect | 3121261 | 17216251 |  | 26338171 | 46675683 | 46675683 | 2613265.358 | Retrocommissioning (RCx) | Heating & Cooling | 1 | Implement ECMs from ComEd report | 0.06 | NA | NA | 0 | 1032975.088 | 1032975.06 | 1580290.27 | 1580290.26
2 | 222 N LaSalle | 1018838 | EEEO | Elect | 3121261 | 16183276 | 16183275.94 | 24757881 | 41222339 | 44062417.642 | 44062.417 | Converge Network People counters | Heating & Cooling & Base | 2 | Technology enablement - Access control Converge Network People counters | 0.001 | NA | NA | 3121.261 | 16183.276 | 16183.276 | 24757.88 | 24757.881
3 | 222 N LaSalle | 1018838 | EEEO | Elect | 3118140 | 16167093 | 16167092.724 | 24733123 | 35774449 | 44018355.225 | 818004.322 | BMS Expansion and optimizations | Heating & Cooling | 3 | Chiller plant instrumentation | 0.02 | NA | NA | 0 | 323341.862 | 323341.86 | 494662.46 | 494662.46
4 | 222 N LaSalle | 1018838 | EEEO | Elect | 3118140 | 15843751 | 15843751.14 | 24238461 | 30497879 | 43200350.903 | 316875.025 | CHW Pumping VFD Retrofit | Cooling | 4 | Add FVD's to CHW and CW pumps | 0.02 | NA | NA | 0 | 316875.025 | 316875.02 | 0
5 | 222 N LaSalle | 1018838 | EEEO | Elect | 3118140 | 15526876 | 15526875.98 | 24238461 | 24904434 | 42883475.878 | 397653.372 | Fan powered box retrofit | Heating & Cooling | 5 | Add DDC, ECM Motors and sensors | 0.01 | NA | NA | 0 | 155268.762 | 155268.76 | 242384.61 | 242384.61
6 | 222 N LaSalle | 1018838 | EEEO | Elect | 3118140 | 15371607 | 15371607.24 | 23996076 | 19398105 | 42485822.506 | 78735.365 | Façade / Window air stopping | Heating & Cooling | 6 | caulking and general air stopping | 0.002 | NA | NA | 0 | 30743.215 | 30743.214 | 47992.15 | 47992.152
7 | 222 N LaSalle | 1018838 | EEEO | Elect | 3118140 | 15340864 |  | 23948084 | 13909025 | 42407087.141 | 15590.698 | Elevator energy revovery | Base | 7 | Optional add to elevator package | 0.005 | NA | NA | 15590.698 | 0 |  | 0
8 | 222 N LaSalle | 1018838 | EEEO | Elect | 3102549 | 15340864 | 15340864 | 23948084 | 8404354 | 42391496.443 | 19644.472 | Roof replacment | Heating & Cooling | 8 | EOL replacement adding insulation | 0.0005 | NA | NA | 0 | 7670.432 | 7670.432 | 11974.04 | 11974.042
9 | 222 N LaSalle | 1018838 | EEEO | Elect | 3102549 | 15333194 |  | 23936110 | 2903987 | 42371851.971 | 62050.977 | Solar | Base | 9 | Rooftop solar | 0.02 | NA | NA | 62050.977 | 0 |  | 0
10 | 222 N LaSalle | 1018838 | EEEO | Elect | 3040498 | 15333194 |  | 23936110 | -2658431 | 42309800.994 | 1196805.49 | Heat recovery for winter operation | Heating | 9.2 | AHU Recovery coils for OA | 0.05 | NA | NA | 0 | 0 |  | 1196805.49 | 1196805.5
11 | 222 N LaSalle | 1018838 | EEEO | Elect | 3040498 | 15333194 | 15333194 | 22739304 | -7024043 | 41112995.504 | 1142174.944 | New High Efficiency Windows | Heating & Cooling | 9.3 | High Eff Windows | 0.03 | NA | NA | 0 | 459995.814 | 459995.82 | 682179.13 | 682179.12
12 | 222 N LaSalle | 1018838 | EEEO | Elect | 3040498 | 14873198 | 14873198.18 | 22057125 | -11167472 | 52280467.504 | 297463.96 | New High Efficiency Electric 1300ton Chiller | Cooling | 9.4 | Chiller EOL Replacement | 0.02 | NA | NA | 0 | 297463.96 | 297463.96 | 0
Showing 1 to 12 of 12 entries, 17 total columns