## One Fed
Building Level Interventions
Instructions: Enter any identified building-level interventions that impact energy usage and emissions. Interventions may include operational changes, retrofits, enhancements to existing capital plans, electrification, and on-site renewables. All boxes for a given intervention should be populated. To optimize for user friendliness, order the interventions based on the earliest possible year of intervention, moving from earliest to latest. Interventions should be identified by the building's engineering team in coordination with Paul Rode and the TS sustainability team. Formatting: Additional Up-Front Costs and Additional Opex should be stated in negative terms and should be priced on a "relative to business as usual" basis (i.e. only state the price in excess of a business as usual scenario). If there is no lifespan, enter "No Lifespan" to indicate this. If the building does not use a certain energy type, enter "0" for the expected reduction. Change in energy consumption should be entered as a negative value if there is a reduction in consumption associated with the intervention and as a positive value if there will be an increase in consumption. If there is an earliest possible date when an intervention can be launched, enter this year in the "Earliest Possible Date" column. If not, enter the current year in this field.
Building | Savings | Order | Intervention Name | Description of Measure | Intervention Type | Additional Up-Front Cost (Net rebates from utilities or state energy offices, or federal programs) | Up Front Cost: Capex or R&M | Change in Electricity Consumption Reduction (kWh) | Change in Natural Gas Use(MMBtu) | Change in Steam Consumption, kLbs | Useful Life/Lifespan | Earliest Possible Year | Change in Opex (O&M) | Energy Savings Passthrough? | Sources (Citations, Links, Consulting Reports, etc.)
222 N LaSalle | Heating & Cooling | 1 | Retrocommissioning (RCx) | Implement ECMs from ComEd report | Retrofit + Training | 48000 | R&M | 138708 |  |  | 10 | 2025 | 0 |  | Engineering
222 N LaSalle | Heating & Cooling & Base | 2 | Technology enablement - Access control Converge Network People counters |  | Capital Project | 2083660 | Capex | 0 |  |  | 15 | 2025 |  |  | Engineering
222 N LaSalle | Heating & Cooling | 3 | BMS Expansion and optimizations | Chiller plant instrumentation | Capex | 500000 | Capex | 2059819 |  |  | 15 | 2026 | -15000 |  | Engineering
222 N LaSalle | Cooling | 4 | CHW Pumping VFD Retrofit | Add FVD's to CHW and CW pumps | Capex | 275000 | Capex | 230692 |  |  | 20 | 2025 |  |  | Engineering
222 N LaSalle | Heating & Cooling | 5 | Fan powered box retrofit | Add DDC, ECM Motors and sensors | Capital Project Enhancement | 2880000 | Capex | 572081 |  |  | 20 | 2028 |  |  | Engineering
222 N LaSalle | Heating & Cooling | 6 | Façade / Window air stopping | caulking and general air stopping | Retrofit | 1300000 | R&M | 108695 |  |  | 15 | 2025 |  |  | Engineering
222 N LaSalle | Base | 7 | Elevator energy revovery | Optional add to elevator package | Capital Project Enhancement | 120000 | Capex | 19881 |  |  | 20 | 2025 |  |  | Engineering
222 N LaSalle | Heating & Cooling | 8 | Roof replacment | EOL replacement adding insulation | Capital Project | 7958000 | Capex | 215217 |  |  | 35 | 2029 |  |  | Engineering
222 N LaSalle | Base | 9 | Solar | Rooftop solar | Capital Project | 400000 | Capex | 169502 |  |  | 25 | 2030 |  |  | Engineering
222 N LaSalle | Base | 9.1 | POU hot water heaters | Restroom DHW POU with planed refresh | Capital Project Enhancement | 196000 | Capex | 16093 |  |  | 15 | 2025 |  |  | Engineering
222 N LaSalle | Heating | 9.2 | Heat recovery for winter operation | AHU Recovery coils for OA | Capital Project | 2100000 | Capex | 32529 |  |  | 35 | 2025 |  |  | Engineering
222 N LaSalle | Heating & Cooling | 9.3 | New High Efficiency Windows | High Eff Windows | Capex | 54100000 | Capex | 525655 |  |  | 40 | 2035 |  |  | Engineering
222 N LaSalle | Cooling | 9.4 | New High Efficiency Electric 1300ton Chiller | Chiller EOL Replacement | Capital Project Enhancement | 1950000 | Capex | 383791 |  |  | 35 | 2030 |  |  | Engineering

## Sheet1
Heating
Cooling
Base
Heating & Cooling
Heating & Cooling & Base